## MOP_E
Report for previous day |  |  |  |  | Date of Reporting: |  | 25-Apr-2023
A. Power Supply Position at All India and Regional level
|  | NR | WR | SR | ER | NER | TOTAL
Demand Met during Evening Peak hrs(MW) (at 20:00 hrs; from RLDCs) |  | 50735 | 59292 | 48950 | 22400 | 2604 | 183981
Peak Shortage (MW) |  | 0 | 0 | 0 | 81 | 63 | 144
Energy Met (MU) |  | 1113 | 1428.2 | 1177.85 | 483.13 | 44.85 | 4247.03
Hydro Gen (MU) |  | 162.95 | 32.61 | 70 | 39.85 | 9.76 | 315.17
Wind Gen (MU) |  | 17.73 | 58.37 | 31.93 | - | - | 108.03
Solar Gen (MU)* |  | 141.76 | 64.47 | 126.17 | 5.53 | 1.38 | 339.31
Energy Shortage (MU) |  | 0.26 | 0 | 0 | 0.87 | 1.4 | 2.53
Maximum Demand Met During the Day (MW) (From NLDC SCADA) |  | 52646 | 65614 | 56756 | 22769 | 2732 | 191917
Time Of Maximum Demand Met (From NLDC SCADA) |  | 19:48 | 15:00 | 15:17 | 18:47 | 18:39 | 11:55
B. Frequency Profile (%)
Region | FVI | < 49.7 | 49.7 - 49.8 | 49.8 - 49.9 | < 49.9 | 49.9 - 50.05 | > 50.05
All India | 0.052 | 0 | 0.47 | 11.28 | 11.76 | 72.01 | 16.24
C. Power Supply Position in States
|  | Max.Demand | Shortage during | Energy Met | Drawal | OD(+)/UD(-) | Max OD | Energy
Region | States | Met during the day(MW) | maximum Demand(MW) | (MU) | Schedule (MU) | (MU) | (MW) | Shortage (MU)
| Punjab | 7185 | 0 | 147.76 | 33.4 | -1.2 | 85 | 0
| Haryana | 7852 | 0 | 149.93 | 87.13 | -1.68 | 190 | 0
| Rajasthan | 12866 | 0 | 259.56 | 63.73 | -3.54 | 128 | 0
| Delhi | 4082 | 0 | 86.21 | 79.57 | -2.39 | 50 | 0
NR | UP | 16209 | 0 | 334.58 | 133.19 | -0.81 | 465 | 0
| Uttarakhand | 1999 | 0 | 40.88 | 20.89 | 0.54 | 259 | 0
| HP | 1636 | 0 | 30.01 | 14.9 | -0.51 | 82 | 0
| J&K(UT) & Ladakh(UT) | 2637 | 0 | 55.7 | 44.64 | 0.01 | 220 | 0.26
| Chandigarh | 209 | 0 | 4.54 | 4.71 | -0.17 | 15 | 0
| Railways_NR ISTS | 171 | 0 | 3.66 | 3.32 | 0.34 | 26 | 0
| Chhattisgarh | 4420 | 0 | 101.8 | 41.9 | -1.7 | 104 | 0
| Gujarat | 20870 | 0 | 440.3 | 230.1 | -1.7 | 672 | 0
| MP | 10384 | 0 | 230.6 | 126 | -2.7 | 561 | 0
WR | Maharashtra | 27068 | 0 | 582.7 | 206.3 | -1.5 | 834 | 0
| Goa | 708 | 0 | 13.3 | 14.9 | -2 | 46 | 0
| DNHDDPDCL | 1270 | 0 | 29 | 29.6 | -0.6 | 25 | 0
| AMNSIL | 828 | 0 | 18.1 | 7.8 | 0.2 | 249 | 0
| BALCO | 520 | 0 | 12.4 | 12.5 | -0.1 | 8 | 0
| Andhra Pradesh | 10745 | 0 | 220.18 | 99.24 | -1.76 | 613 | 0
| Telangana | 9894 | 0 | 197.91 | 74.83 | -1.07 | 510 | 0
SR | Karnataka | 15361 | 0 | 294.07 | 118.99 | -0.53 | 734 | 0
| Kerala | 4675 | 0 | 96.23 | 73.14 | -0.18 | 280 | 0
| Tamil Nadu | 17066 | 0 | 359.52 | 220.48 | -2.2 | 429 | 0
| Puducherry | 437 | 0 | 9.94 | 9.94 | -0.69 | 7 | 0
| Bihar | 5543 | 0 | 98.33 | 91.45 | -2.78 | 575 | 0.79
| DVC | 3519 | 0 | 73.74 | -41.71 | -1.32 | 246 | 0
| Jharkhand | 1523 | 0 | 29.48 | 24.95 | -3.71 | 184 | 0.08
ER | Odisha | 5989 | 0 | 115.79 | 48.05 | -1.78 | 407 | 0
| West Bengal | 7429 | 0 | 164.46 | 35.86 | -4.93 | 120 | 0
| Sikkim | 94 | 0 | 1.33 | 1.33 | 0 | 62 | 0
| Arunachal Pradesh | 149 | 0 | 2.19 | 2.36 | -0.26 | 79 | 0
| Assam | 1678 | 0 | 26.51 | 20.16 | -0.39 | 89 | 0
| Manipur | 182 | 0 | 2.42 | 2.44 | -0.02 | 36 | 0
NER | Meghalaya | 306 | 63 | 5.02 | 3.58 | -0.08 | 72 | 1.4
| Mizoram | 113 | 0 | 1.81 | 1.47 | -0.3 | 8 | 0
| Nagaland | 146 | 0 | 2.03 | 2.13 | -0.1 | 13 | 0
| Tripura | 277 | 0 | 4.87 | 4.27 | -0.07 | 56 | 0
D. Transnational Exchanges (MU) - Import(+ve)/Export(-ve)
|  | Bhutan | Nepal | Bangladesh | Godda -> Bangladesh
Actual (MU) |  | 0.5703 | -12.444 | -23.344 | -11.25
Day Peak (MW) |  | 36 | -641.37 | -1092 | -560
E. Import/Export by Regions (in MU) - Import(+ve)/Export(-ve); OD(+)/UD(-)
|  | NR | WR | SR | ER | NER | TOTAL
Schedule(MU) |  | 87.04 | -173.46 | 193.91 | -103.9 | -3.59 | 0
Actual(MU) |  | 58.61 | -155.27 | 213.336 | -118.78 | -1.95 | -4.054
O/D/U/D(MU) |  | -28.43 | 18.19 | 19.426 | -14.88 | 1.64 | -4.054
F. Generation Outage(MW)
|  | NR | WR | SR | ER | NER | TOTAL | % Share
Central Sector |  | 4187.04 | 8110.6 | 3538 | 1550 | 425 | 17810.64 | 44.5342
State Sector |  | 5689.5 | 11390 | 3568 | 1290 | 245 | 22182.5 | 55.4658
Total |  | 9876.54 | 19500.6 | 7106 | 2840 | 670 | 39993.14 | 100
G. Sourcewise generation (Gross) (MU)
|  | NR | WR | SR | ER | NER | All India | % Share
Coal |  | 715.26 | 1473.64 | 682.12 | 642.47 | 12.58 | 3526.07 | 76.3733
Lignite |  | 23.35 | 18.69 | 51.86 | 0 | 0 | 93.9 | 2.0338
Hydro |  | 162.95 | 32.61 | 70 | 39.85 | 9.76 | 315.17 | 6.8265
Nuclear |  | 30.02 | 36.22 | 45.05 | 0 | 0 | 111.29 | 2.4105
Gas, Naptha & Diesel |  | 17.6 | 18.43 | 6.4 | 0 | 29.71 | 72.14 | 1.5625
RES (Wind, Solar, Biomass & Others) |  | 179.35 | 124.06 | 187.58 | 5.95 | 1.38 | 498.32 | 10.7934
Total |  | 1128.53 | 1703.65 | 1043.01 | 688.27 | 53.43 | 4616.89 | 100
Share of RES in total generation (%) |  | 15.8924 | 7.282 | 17.9845 | 0.86449 | 2.5828 | 10.7934
Share of Non-fossil fuel (Hydro,Nuclear and RES) in total generation(%) |  | 32.9916 | 11.3222 | 29.0151 | 6.6544 | 20.8497 | 20.0304
H. All India Demand Diversity Factor
Based on Regional Max Demands |  | 1.0448
Based on State Max Demands |  | 1.0736
Diversity factor = Sum of regional or state maximum demands / All India maximum demand
*Source: RLDCs for solar connected to ISTS; SLDCs for embedded solar. Limited visibility of embedded solar data.
**Note: All generation MU figures are gross
***Godda (Jharkhand) -> Bangladesh power exchange is through the radial connection (isolated from Indian Grid)
Executive Director-NLDC

## IR-Line
INTER-REGIONAL EXCHANGES
Import=(+ve) /Export =(-ve) for NET (MU)
[6 empty] | Date of Reporting: |  |  | 25-Apr-2023
Sl No | Voltage Level | Line Details | No. of Circuit | Max Import (MW) | Max Export (MW) | Import (MU) | Export (MU) |  | NET (MU)
Import/Export of ER (With NR)
1 | HVDC | ALIPURDUAR-AGRA | 2 | 0 | 0 | 0 | 0 |  | 0
2 | HVDC | PUSAULI B/B | - | 0 | 97 | 0 | 2.31 |  | -2.31
3 | 765 kV | GAYA-VARANASI | 2 | 222 | 797 | 0 | 8.46 |  | -8.46
4 | 765 kV | SASARAM-FATEHPUR | 1 | 32 | 586 | 0 | 6.16 |  | -6.16
5 | 765 kV | GAYA-BALIA | 1 | 0 | 575 | 0 | 8.09 |  | -8.09
6 | 400 kV | PUSAULI-VARANASI | 1 | 9 | 88 | 0 | 0.99 |  | -0.99
7 | 400 kV | PUSAULI -ALLAHABAD | 1 | 0 | 116 | 0 | 1.32 |  | -1.32
8 | 400 kV | MUZAFFARPUR-GORAKHPUR | 2 | 174 | 675 | 0 | 6.09 |  | -6.09
9 | 400 kV | PATNA-BALIA | 2 | 0 | 452 | 0 | 6.21 |  | -6.21
10 | 400 kV | NAUBATPUR-BALIA | 2 | 14 | 467 | 0 | 6.15 |  | -6.15
11 | 400 kV | BIHARSHARIFF-BALIA | 2 | 207 | 264 | 0 | 1.14 |  | -1.14
12 | 400 kV | MOTIHARI-GORAKHPUR | 2 | 28 | 495 | 0 | 6.07 |  | -6.07
13 | 400 kV | BIHARSHARIFF-VARANASI | 2 | 95 | 338 | 0 | 3.35 |  | -3.35
14 | 220 kV | SAHUPURI-KARAMNASA | 1 | 0 | 143 | 0 | 2.15 |  | -2.15
15 | 132 kV | NAGAR UNTARI-RIHAND | 1 | 0 | 0 | 0 | 0 |  | 0
16 | 132 kV | GARWAH-RIHAND | 1 | 25 | 0 | 0.26 | 0 |  | 0.26
17 | 132 kV | KARMANASA-SAHUPURI | 1 | 0 | 29 | 0 | 0 |  | 0
18 | 132 kV | KARMANASA-CHANDAULI | 1 | 0 | 0 | 0 | 0 |  | 0
ER-NR | [5 empty] | 0.26 | 58.49 |  | -58.23
Import/Export of ER (With WR)
1 | 765 kV | JHARSUGUDA-DHARAMJAIGARH | 4 | 1768 | 139 | 17.54 | 0 |  | 17.54
2 | 765 kV | NEW RANCHI-DHARAMJAIGARH | 2 | 227 | 749 | 0 | 5.26 |  | -5.26
3 | 765 kV | JHARSUGUDA-DURG | 2 | 0 | 624 | 0 | 9.85 |  | -9.85
4 | 400 kV | JHARSUGUDA-RAIGARH | 4 | 0 | 485 | 0 | 11.19 |  | -11.19
5 | 400 kV | RANCHI-SIPAT | 2 | 41 | 322 | 0 | 2.15 |  | -2.15
6 | 220 kV | BUDHIPADAR-RAIGARH | 1 | 0 | 56 | 0 | 0.95 |  | -0.95
7 | 220 kV | BUDHIPADAR-KORBA | 2 | 122 | 0 | 2.64 | 0 |  | 2.64
ER-WR | [5 empty] | 20.18 | 29.4 |  | -9.22
Import/Export of ER (With SR)
1 | HVDC | JEYPORE-GAZUWAKA B/B | 2 | 0 | 439 | 0 | 10.42 |  | -10.42
2 | HVDC | TALCHER-KOLAR BIPOLE | 2 | 0 | 1655 | 0 | 39.62 |  | -39.62
3 | 765 kV | ANGUL-SRIKAKULAM | 2 | 0 | 2931 | 0 | 59.75 |  | -59.75
4 | 400 kV | TALCHER-I/C | 2 | 255 | 320 | 3.16 | 0 |  | 3.16
5 | 220 kV | BALIMELA-UPPER-SILERRU | 1 | 0 | 0 | 0 | 0 |  | 0
ER-SR | [5 empty] | 0 | 109.79 |  | -109.79
Import/Export of ER (With NER)
1 | 400 kV | BINAGURI-BONGAIGAON | 2 | 178 | 15 | 2.2 | 0 |  | 2.2
2 | 400 kV | ALIPURDUAR-BONGAIGAON | 2 | 610 | 0 | 8.98 | 0 |  | 8.98
3 | 220 kV | ALIPURDUAR-SALAKATI | 2 | 114 | 0 | 1.8 | 0 |  | 1.8
ER-NER | [5 empty] | 12.98 | 0 |  | 12.98
Import/Export of NER (With NR)
1 | HVDC | BISWANATH CHARIALI-AGRA | 2 | 482 | 0 | 11.47 | 0 |  | 11.47
NER-NR | [5 empty] | 11.47 | 0 |  | 11.47
Import/Export of WR (With NR)
1 | HVDC | CHAMPA-KURUKSHETRA | 2 | 5 | 1501 | 0 | 20.21 |  | -20.21
2 | HVDC | VINDHYACHAL B/B | - | 442 | 0 | 12.19 | 0 |  | 12.19
3 | HVDC | MUNDRA-MOHINDERGARH | 2 | 0 | 305 | 0 | 0.62 |  | -0.62
4 | 765 kV | GWALIOR-AGRA | 2 | 0 | 1377 | 0 | 22.21 |  | -22.21
5 | 765 kV | GWALIOR-PHAGI | 2 | 463 | 1519 | 1.84 | 19.99 |  | -18.15
6 | 765 kV | JABALPUR-ORAI | 2 | 178 | 649 | 0 | 14.84 |  | -14.84
7 | 765 kV | GWALIOR-ORAI | 1 | 933 | 0 | 15.77 | 0 |  | 15.77
8 | 765 kV | SATNA-ORAI | 1 | 0 | 920 | 0 | 17.81 |  | -17.81
9 | 765 kV | BANASKANTHA-CHITORGARH | 2 | 2790 | 0 | 39.25 | 0 |  | 39.25
10 | 765 kV | VINDHYACHAL-VARANASI | 2 | 0 | 1949 | 0 | 34.91 |  | -34.91
11 | 400 kV | ZERDA-KANKROLI | 1 | 537 | 43 | 7.33 | 0 |  | 7.33
12 | 400 kV | ZERDA -BHINMAL | 1 | 894 | 0 | 10.53 | 0 |  | 10.53
13 | 400 kV | VINDHYACHAL -RIHAND | 1 | 960 | 0 | 21.8 | 0 |  | 21.8
14 | 400 kV | RAPP-SHUJALPUR | 2 | 692 | 200 | 5.02 | 1.7 |  | 3.32
15 | 220 kV | BHANPURA-RANPUR | 1 | 0 | 0 | 0 | 0 |  | 0
16 | 220 kV | BHANPURA-MORAK | 1 | 0 | 30 | 0 | 0 |  | 0
17 | 220 kV | MEHGAON-AURAIYA | 1 | 66 | 0 | 0.73 | 0 |  | 0.73
18 | 220 kV | MALANPUR-AURAIYA | 1 | 51 | 0 | 0.68 | 0 |  | 0.68
19 | 132 kV | GWALIOR-SAWAI MADHOPUR | 1 | 0 | 0 | 0 | 0 |  | 0
20 | 132 kV | RAJGHAT-LALITPUR | 2 | 0 | 0 | 0 | 0 |  | 0
WR-NR | [5 empty] | 115.14 | 132.29 |  | -17.15
Import/Export of WR (With SR)
1 | HVDC | BHADRAWATI B/B | - | 0 | 1009 | 0 | 14.25 |  | -14.25
2 | HVDC | RAIGARH-PUGALUR | 2 | 0 | 6021 | 0 | 103.72 |  | -103.72
3 | 765 kV | SOLAPUR-RAICHUR | 2 | 328 | 1354 | 0.29 | 12.72 |  | -12.43
4 | 765 kV | WARDHA-NIZAMABAD | 2 | 0 | 2330 | 0 | 39.24 |  | -39.24
5 | 400 kV | KOLHAPUR-KUDGI | 2 | 1041 | 0 | 19.83 | 0 |  | 19.83
6 | 220 kV | KOLHAPUR-CHIKODI | 2 | 0 | 0 | 0 | 0 |  | 0
7 | 220 kV | PONDA-AMBEWADI | 1 | 0 | 0 | 0 | 0 |  | 0
8 | 220 kV | XELDEM-AMBEWADI | 1 | 0 | 126 | 2.58 | 0 |  | 2.58
WR-SR | [5 empty] | 22.7 | 169.93 |  | -147.23
INTERNATIONAL EXCHANGES | [7 empty] | Import(+ve)/Export(-ve)
State |  | Region | Line Name |  | Max (MW) | Min (MW) | Avg (MW) |  | Energy Exchange (MU)
|  | ER | 400kV MANGDECHHU-ALIPURDUAR 1,2&3 i.e. ALIPURDUAR RECEIPT (from MANGDECHU HEP 4*180MW) |  | -86.006 | 6.038 | -43.82 |  | -1.0516
|  | ER | 400kV TALA-BINAGURI 1,2,4 (& 400kV MALBASE - BINAGURI) i.e. BINAGURI RECEIPT (from TALA HEP 6*170MW) |  | 324.768 | 212.453 | 264.08 |  | 6.338
BHUTAN |  | ER | 220kV CHUKHA-BIRPARA 1&2 (& 220kV MALBASE - BIRPARA) i.e. BIRPARA RECEIPT (from CHUKHA HEP 4*84MW) |  | -214.323 | -126.811 | -184.13 |  | -4.419
|  | NER | 132kV GELEPHU-SALAKATI |  | -23 | -6 | -17.008 |  | -0.4082
|  | NER | 132kV MOTANGA-RANGIA |  | 7 | 0 | 4.521 |  | 0.1085
|  | NR | 132kV MAHENDRANAGAR-TANAKPUR(NHPC) |  | -75 | 0 | -61 |  | -1.46
NEPAL |  | ER | NEPAL IMPORT (FROM BIHAR) |  | -95.37 | -72.39 | -81.833 |  | -1.964
|  | ER | 400kV DHALKEBAR-MUZAFFARPUR 1&2 |  | -471 | -222 | -375.833 |  | -9.02
|  | ER | BHERAMARA B/B HVDC (B'DESH) |  | -942 | -699 | -846.83 |  | -20.324
BANGLADESH |  | ER (Isolated from Indian Grid) | 400kV GODDA_TPS-RAHANPUR (B'DESH) D/C |  | -560 | -344 | -468.75 |  | -11.25
|  | NER | 132kV COMILLA-SURAJMANI NAGAR 1&2 |  | -150 | 0 | -125.8333 |  | -3.02