## MOP_E
Report for previous day |  |  |  |  | Date of Reporting: |  | 28-Apr-2023
A. Power Supply Position at All India and Regional level
|  | NR | WR | SR | ER | NER | TOTAL
Demand Met during Evening Peak hrs(MW) (at 20:00 hrs; from RLDCs) |  | 52217 | 58439 | 49111 | 23678 | 2867 | 186312
Peak Shortage (MW) |  | 80 | 0 | 0 | 0 | 18 | 98
Energy Met (MU) |  | 1212 | 1391.6 | 1174.94 | 528.94 | 53.11 | 4360.59
Hydro Gen (MU) |  | 179.12 | 27.32 | 75.9 | 36.61 | 7.56 | 326.51
Wind Gen (MU) |  | 14.51 | 69.63 | 31.63 | - | - | 115.77
Solar Gen (MU)* |  | 100.29 | 63.97 | 109.48 | 2.53 | 1.16 | 277.43
Energy Shortage (MU) |  | 0.24 | 0 | 0 | 1.106 | 1.52 | 2.866
Maximum Demand Met During the Day (MW) (From NLDC SCADA) |  | 54108 | 64466 | 55896 | 24205 | 2908 | 196240
Time Of Maximum Demand Met (From NLDC SCADA) |  | 00:00 | 15:11 | 11:22 | 00:01 | 18:41 | 15:00
B. Frequency Profile (%)
Region | FVI | < 49.7 | 49.7 - 49.8 | 49.8 - 49.9 | < 49.9 | 49.9 - 50.05 | > 50.05
All India | 0.055 | 0.03 | 0.96 | 8.99 | 9.99 | 71.65 | 18.37
C. Power Supply Position in States
|  | Max.Demand | Shortage during | Energy Met | Drawal | OD(+)/UD(-) | Max OD | Energy
Region | States | Met during the day(MW) | maximum Demand(MW) | (MU) | Schedule (MU) | (MU) | (MW) | Shortage (MU)
| Punjab | 7153 | 0 | 153.1 | 34.49 | -1 | 107 | 0
| Haryana | 7615 | 0 | 159.27 | 100.79 | -1.97 | 272 | 0
| Rajasthan | 13190 | 0 | 265.14 | 81.71 | -4.91 | 271 | 0
| Delhi | 4626 | 0 | 94.11 | 88.22 | -3.23 | 24 | 0.04
NR | UP | 18966 | 0 | 406.77 | 153.27 | -1.1 | 359 | 0
| Uttarakhand | 2023 | 0 | 43.16 | 26.35 | -0.7 | 193 | 0.08
| HP | 1576 | 4 | 30 | 14.37 | -0.6 | 75 | 0.05
| J&K(UT) & Ladakh(UT) | 2839 | 0 | 52.49 | 36.19 | -0.04 | 169 | 0.07
| Chandigarh | 218 | 0 | 4.49 | 4.76 | -0.27 | 12 | 0
| Railways_NR ISTS | 171 | 0 | 3.82 | 3.18 | 0.64 | 42 | 0
| Chhattisgarh | 4791 | 0 | 107.2 | 51.9 | -2.3 | 187 | 0
| Gujarat | 21064 | 0 | 447.3 | 217.6 | -1.3 | 633 | 0
| MP | 10210 | 0 | 210.8 | 101.5 | -1.7 | 541 | 0
WR | Maharashtra | 25976 | 0 | 551.1 | 204.8 | -2.5 | 758 | 0
| Goa | 717 | 0 | 15.3 | 15.2 | -0.5 | 45 | 0
| DNHDDPDCL | 1238 | 0 | 28.3 | 28.4 | -0.1 | 54 | 0
| AMNSIL | 857 | 0 | 19.2 | 8.3 | 0.1 | 294 | 0
| BALCO | 520 | 0 | 12.4 | 12.4 | 0 | 9 | 0
| Andhra Pradesh | 11505 | 0 | 232.94 | 95.77 | -1.63 | 380 | 0
| Telangana | 8623 | 0 | 177.85 | 55.91 | -0.55 | 485 | 0
SR | Karnataka | 15188 | 0 | 289.54 | 122.1 | 0.39 | 757 | 0
| Kerala | 4366 | 0 | 90.13 | 70.41 | -0.38 | 266 | 0
| Tamil Nadu | 17282 | 0 | 374.58 | 231.56 | -0.74 | 404 | 0
| Puducherry | 453 | 0 | 9.9 | 9.99 | -0.83 | 46 | 0
| Bihar | 6055 | 0 | 114.82 | 105.64 | -1.24 | 307 | 0.629
| DVC | 3728 | 0 | 77.85 | -46.91 | 0.34 | 282 | 0
| Jharkhand | 1719 | 0 | 32.83 | 27.12 | -1.27 | 267 | 0.477
ER | Odisha | 5874 | 0 | 119.86 | 42.29 | -0.81 | 447 | 0
| West Bengal | 8912 | 0 | 181.98 | 52.1 | -4.8 | 293 | 0
| Sikkim | 93 | 0 | 1.49 | 1.32 | 0.17 | 67 | 0
| Arunachal Pradesh | 158 | 0 | 2.77 | 2.21 | 0.47 | 63 | 0
| Assam | 1885 | 0 | 33.35 | 27.07 | 0.12 | 151 | 0
| Manipur | 199 | 0 | 2.64 | 2.59 | 0.05 | 25 | 0
NER | Meghalaya | 306 | 65 | 5.06 | 3.34 | 0.02 | 71 | 1.52
| Mizoram | 119 | 0 | 1.93 | 1.44 | -0.14 | 11 | 0
| Nagaland | 152 | 0 | 2.42 | 2.4 | -0.04 | 10 | 0
| Tripura | 267 | 0 | 4.94 | 4.64 | 0.22 | 85 | 0
D. Transnational Exchanges (MU) - Import(+ve)/Export(-ve)
|  | Bhutan | Nepal | Bangladesh | Godda -> Bangladesh
Actual (MU) |  | -3.4173 | -15.586 | -15.983 | -7.3
Day Peak (MW) |  | -229.11 | -707.9 | -1061 | -546
E. Import/Export by Regions (in MU) - Import(+ve)/Export(-ve); OD(+)/UD(-)
|  | NR | WR | SR | ER | NER | TOTAL
Schedule(MU) |  | 159.31 | -235.38 | 185.32 | -114.18 | 4.93 | 0
Actual(MU) |  | 152.94 | -218.37 | 186.769 | -130.59 | 5.98 | -3.271
O/D/U/D(MU) |  | -6.37 | 17.01 | 1.449 | -16.41 | 1.05 | -3.271
F. Generation Outage(MW)
|  | NR | WR | SR | ER | NER | TOTAL | % Share
Central Sector |  | 4537.04 | 7880.6 | 2788 | 1390 | 446 | 17042 | 43.0354
State Sector |  | 4734.5 | 10734.5 | 5256 | 1290 | 314 | 22330 | 56.9646
Total |  | 9271.54 | 18615.1 | 8044 | 2680 | 760 | 39371 | 100
G. Sourcewise generation (Gross) (MU)
|  | NR | WR | SR | ER | NER | All India | % Share
Coal |  | 765.06 | 1490.58 | 707.82 | 704.1 | 15.75 | 3683.31 | 77.6848
Lignite |  | 25.74 | 20.81 | 57.61 | 0 | 0 | 104.16 | 2.1968
Hydro |  | 179.12 | 27.32 | 75.9 | 36.61 | 7.56 | 326.51 | 6.8864
Nuclear |  | 28.63 | 37.01 | 47.59 | 0 | 0 | 113.23 | 2.3881
Gas, Naptha & Diesel |  | 15.99 | 20.58 | 6.3 | 0 | 28.69 | 71.56 | 1.5093
RES (Wind, Solar, Biomass & Others) |  | 134.61 | 134.56 | 168.35 | 2.85 | 1.16 | 442 | 9.3345
Total |  | 1149.15 | 1731 | 1063.57 | 743.56 | 53.16 | 4740 | 100
Share of RES in total generation (%) |  | 11.7139 | 7.77 | 15.8288 | 0.38329 | 2.1821 | 9.3144
Share of Non-fossil fuel (Hydro,Nuclear and RES) in total generation(%) |  | 29.7925 | 11.49 | 27.4397 | 5.3069 | 16.4033 | 18.591
H. All India Demand Diversity Factor
Based on Regional Max Demands |  | 1.0272
Based on State Max Demands |  | 1.0735
Diversity factor = Sum of regional or state maximum demands / All India maximum demand
*Source: RLDCs for solar connected to ISTS; SLDCs for embedded solar. Limited visibility of embedded solar data.
**Note: All generation MU figures are gross
***Godda (Jharkhand) -> Bangladesh power exchange is through the radial connection (isolated from Indian Grid)
Executive Director-NLDC

## IR-Line
INTER-REGIONAL EXCHANGES
Import=(+ve) /Export =(-ve) for NET (MU)
[6 empty] | Date of Reporting: |  |  | 28-Apr-2023
Sl No | Voltage Level | Line Details | No. of Circuit | Max Import (MW) | Max Export (MW) | Import (MU) | Export (MU) |  | NET (MU)
Import/Export of ER (With NR)
1 | HVDC | ALIPURDUAR-AGRA | 2 | 0 | 0 | 0 | 0 |  | 0
2 | HVDC | PUSAULI B/B | - | 0 | 97 | 0 | 2.53 |  | -2.53
3 | 765 kV | GAYA-VARANASI | 2 | 0 | 710 | 0 | 11.3 |  | -11.3
4 | 765 kV | SASARAM-FATEHPUR | 1 | 0 | 497 | 0 | 8.45 |  | -8.45
5 | 765 kV | GAYA-BALIA | 1 | 0 | 583 | 0 | 11.32 |  | -11.32
6 | 400 kV | PUSAULI-VARANASI | 1 | 15 | 65 | 0 | 0.44 |  | -0.44
7 | 400 kV | PUSAULI -ALLAHABAD | 1 | 0 | 109 | 0 | 1.92 |  | -1.92
8 | 400 kV | MUZAFFARPUR-GORAKHPUR | 2 | 128 | 685 | 0 | 6.01 |  | -6.01
9 | 400 kV | PATNA-BALIA | 2 | 0 | 536 | 0 | 10.5 |  | -10.5
10 | 400 kV | NAUBATPUR-BALIA | 2 | 0 | 562 | 0 | 9.04 |  | -9.04
11 | 400 kV | BIHARSHARIFF-BALIA | 2 | 166 | 289 | 0 | 0.98 |  | -0.98
12 | 400 kV | MOTIHARI-GORAKHPUR | 2 | 0 | 440 | 0 | 6.75 |  | -6.75
13 | 400 kV | BIHARSHARIFF-VARANASI | 2 | 5 | 331 | 0 | 4.17 |  | -4.17
14 | 220 kV | SAHUPURI-KARAMNASA | 1 | 0 | 171 | 0 | 2.87 |  | -2.87
15 | 132 kV | NAGAR UNTARI-RIHAND | 1 | 0 | 0 | 0 | 0 |  | 0
16 | 132 kV | GARWAH-RIHAND | 1 | 25 | 0 | 0.38 | 0 |  | 0.38
17 | 132 kV | KARMANASA-SAHUPURI | 1 | 0 | 0 | 0 | 0 |  | 0
18 | 132 kV | KARMANASA-CHANDAULI | 1 | 0 | 0 | 0 | 0 |  | 0
ER-NR | [5 empty] | 0.38 | 76.28 |  | -75.9
Import/Export of ER (With WR)
1 | 765 kV | JHARSUGUDA-DHARAMJAIGARH | 4 | 1224 | 0 | 14.8 | 0 |  | 14.8
2 | 765 kV | NEW RANCHI-DHARAMJAIGARH | 2 | 706 | 700 | 2.82 | 0 |  | 2.82
3 | 765 kV | JHARSUGUDA-DURG | 2 | 0 | 532 | 0 | 8.85 |  | -8.85
4 | 400 kV | JHARSUGUDA-RAIGARH | 4 | 0 | 564 | 0 | 8.44 |  | -8.44
5 | 400 kV | RANCHI-SIPAT | 2 | 160 | 196 | 0 | 0.27 |  | -0.27
6 | 220 kV | BUDHIPADAR-RAIGARH | 1 | 0 | 56 | 0 | 1.51 |  | -1.51
7 | 220 kV | BUDHIPADAR-KORBA | 2 | 83 | 0 | 1.07 | 0 |  | 1.07
ER-WR | [5 empty] | 18.69 | 19.07 |  | -0.38
Import/Export of ER (With SR)
1 | HVDC | JEYPORE-GAZUWAKA B/B | 2 | 0 | 548 | 0 | 11.89 |  | -11.89
2 | HVDC | TALCHER-KOLAR BIPOLE | 2 | 0 | 1643 | 0 | 39.62 |  | -39.62
3 | 765 kV | ANGUL-SRIKAKULAM | 2 | 0 | 2810 | 0 | 55.4 |  | -55.4
4 | 400 kV | TALCHER-I/C | 2 | 258 | 0 | 4.88 | 0 |  | 4.88
5 | 220 kV | BALIMELA-UPPER-SILERRU | 1 | 0 | 0 | 0 | 0 |  | 0
ER-SR | [5 empty] | 0 | 106.91 |  | -106.91
Import/Export of ER (With NER)
1 | 400 kV | BINAGURI-BONGAIGAON | 2 | 111 | 69 | 0.63 | 0.23 |  | 0.4
2 | 400 kV | ALIPURDUAR-BONGAIGAON | 2 | 440 | 95 | 3.84 | 0 |  | 3.84
3 | 220 kV | ALIPURDUAR-SALAKATI | 2 | 93 | 10 | 0.96 | 0 |  | 0.96
ER-NER | [5 empty] | 5.43 | 0.23 |  | 5.2
Import/Export of NER (With NR)
1 | HVDC | BISWANATH CHARIALI-AGRA | 2 | 482 | 0 | 11.48 | 0 |  | 11.48
NER-NR | [5 empty] | 11.48 | 0 |  | 11.48
Import/Export of WR (With NR)
1 | HVDC | CHAMPA-KURUKSHETRA | 2 | 0 | 1506 | 0 | 34.9 |  | -34.9
2 | HVDC | VINDHYACHAL B/B | - | 441 | 0 | 12.13 | 0 |  | 12.13
3 | HVDC | MUNDRA-MOHINDERGARH | 2 | 0 | 304 | 7.22 | 0 |  | 7.22
4 | 765 kV | GWALIOR-AGRA | 2 | 0 | 2061 | 0 | 31.04 |  | -31.04
5 | 765 kV | GWALIOR-PHAGI | 2 | 0 | 1515 | 0 | 26.04 |  | -26.04
6 | 765 kV | JABALPUR-ORAI | 2 | 0 | 783 | 0 | 22.89 |  | -22.89
7 | 765 kV | GWALIOR-ORAI | 1 | 858 | 0 | 17.43 | 0 |  | 17.43
8 | 765 kV | SATNA-ORAI | 1 | 0 | 888 | 0 | 19.41 |  | -19.41
9 | 765 kV | BANASKANTHA-CHITORGARH | 2 | 1450 | 9 | 18.89 | 0 |  | 18.89
10 | 765 kV | VINDHYACHAL-VARANASI | 2 | 0 | 2522 | 0 | 41.89 |  | -41.89
11 | 400 kV | ZERDA-KANKROLI | 1 | 274 | 0 | 4.33 | 0 |  | 4.33
12 | 400 kV | ZERDA -BHINMAL | 1 | 508 | 27 | 5.58 | 0 |  | 5.58
13 | 400 kV | VINDHYACHAL -RIHAND | 1 | 962 | 0 | 22.1 | 0 |  | 22.1
14 | 400 kV | RAPP-SHUJALPUR | 2 | 249 | 426 | 0.81 | 2.88 |  | -2.07
15 | 220 kV | BHANPURA-RANPUR | 1 | 0 | 0 | 0 | 0 |  | 0
16 | 220 kV | BHANPURA-MORAK | 1 | 0 | 30 | 0 | 1.9 |  | -1.9
17 | 220 kV | MEHGAON-AURAIYA | 1 | 59 | 7 | 0.54 | 0 |  | 0.54
18 | 220 kV | MALANPUR-AURAIYA | 1 | 43 | 19 | 0.31 | 0.04 |  | 0.27
19 | 132 kV | GWALIOR-SAWAI MADHOPUR | 1 | 0 | 0 | 0 | 0 |  | 0
20 | 132 kV | RAJGHAT-LALITPUR | 2 | 0 | 0 | 0 | 0 |  | 0
WR-NR | [5 empty] | 89.34 | 180.99 |  | -91.65
Import/Export of WR (With SR)
1 | HVDC | BHADRAWATI B/B | - | 0 | 1005 | 0 | 24 |  | -24
2 | HVDC | RAIGARH-PUGALUR | 2 | 0 | 5015 | 0 | 87.83 |  | -87.83
3 | 765 kV | SOLAPUR-RAICHUR | 2 | 280 | 1324 | 0.31 | 11.48 |  | -11.17
4 | 765 kV | WARDHA-NIZAMABAD | 2 | 0 | 1884 | 0 | 27.66 |  | -27.66
5 | 400 kV | KOLHAPUR-KUDGI | 2 | 1105 | 0 | 20.93 | 0 |  | 20.93
6 | 220 kV | KOLHAPUR-CHIKODI | 2 | 0 | 0 | 0 | 0 |  | 0
7 | 220 kV | PONDA-AMBEWADI | 1 | 0 | 0 | 0 | 0 |  | 0
8 | 220 kV | XELDEM-AMBEWADI | 1 | 0 | 134 | 2.73 | 0 |  | 2.73
WR-SR | [5 empty] | 23.97 | 150.97 |  | -127
INTERNATIONAL EXCHANGES | [7 empty] | Import(+ve)/Export(-ve)
State |  | Region | Line Name |  | Max (MW) | Min (MW) | Avg (MW) |  | Energy Exchange (MU)
|  | ER | 400kV MANGDECHHU-ALIPURDUAR 1,2&3 i.e. ALIPURDUAR RECEIPT (from MANGDECHU HEP 4*180MW) |  | -126.305 | 16.907 | -75.5 |  | -1.812
|  | ER | 400kV TALA-BINAGURI 1,2,4 (& 400kV MALBASE - BINAGURI) i.e. BINAGURI RECEIPT (from TALA HEP 6*170MW) |  | 319.356 | 64.954 | 160.33 |  | 3.848
BHUTAN |  | ER | 220kV CHUKHA-BIRPARA 1&2 (& 220kV MALBASE - BIRPARA) i.e. BIRPARA RECEIPT (from CHUKHA HEP 4*84MW) |  | -303.337 | -172.87 | -242.88 |  | -5.829
|  | NER | 132kV GELEPHU-SALAKATI |  | 20.89 | 1.47 | 11.779 |  | 0.2827
|  | NER | 132kV MOTANGA-RANGIA |  | 37 | 2.33 | 3.75 |  | 0.09
|  | NR | 132kV MAHENDRANAGAR-TANAKPUR(NHPC) |  | -79 | 0 | -68 |  | -1.64
NEPAL |  | ER | NEPAL IMPORT (FROM BIHAR) |  | -144.9 | -41 | -102.333 |  | -2.456
|  | ER | 400kV DHALKEBAR-MUZAFFARPUR 1&2 |  | -484 | -338 | -478.75 |  | -11.49
|  | ER | BHERAMARA B/B HVDC (B'DESH) |  | -921 | -312 | -559.29 |  | -13.423
BANGLADESH |  | ER (Isolated from Indian Grid) | 400kV GODDA_TPS-RAHANPUR (B'DESH) D/C |  | -546 | 0 | -304.167 |  | -7.3
|  | NER | 132kV COMILLA-SURAJMANI NAGAR 1&2 |  | -140 | 0 | -106.6667 |  | -2.56